Auxiliary Power Systems For Emergency Communications

Ed Harris, KE4SKY, Training Officer Arlington County RACES, and John Bartone, K4KXK, MSEE

Batteries are only temporary power unless you have a sustainable means of recharging, independent from the AC mains.  Photovoltaics (PV) provide sustainable DC power at lower life-cycle cost than generators, when combined with a well -designed battery bank and charge controller.

Attention to POLARITY is always important.  Whenever using battery power, the correct connection sequence is important to avoid sparking or damage to system components.  An arc caused by wiring a connection in the wrong order may ignite hydrogen given off by a battery, causing an explosion!  High current flows at low voltages can still be lethal.  Always disconnect all circuits before working on any power system.

Always follow the correct re-connection sequence:

1     positive connection to battery

2     positive connection to load

3     negative connection to battery

4     negative connection to load

Typical 12-volt lead-acid batteries have a voltage of about 14 volts when fully charged and 11 volts if fully discharged. Typical amateur radio equipment doesn't operate properly below 11.5 volts.  You can't exceed the depth of discharge at which battery voltage under load drops below that figure. Battery systems are current-limited and their capacity is finite. Oversized loads or excessive duty cycle cause rapid depletion of battery capacity.  Battery systems must be sized appropriately to the load to supply the current needed.

Cranking amps tell nothing about how long a battery will run your radio.  Cold Cranking Amps (CCA) represent the current an automotive “starting” battery provides continuously for 30 seconds at 0 degs. F before voltage is drops to 1.7 volts per cell (Vpc) at which it is fully discharged.  In MCA or Marine Cranking Amps, the measurement is taken at 32 degs. F.

Reserve capacity  is the time a starting battery will sustain a continuous 25A load before cell voltage drops to 1.7vpc. This is a bit more useful measure, but less than perferct for our EmCom purpose.

Performance measurements used for rating deep cycle batteries are amp-hour capacity and depth of discharge

(DoD).  Amp-hour capacity is total current available over

time, measured at 80 degs. F.  DoD is the percentage of

capacity available during a charge- discharge cycle.

Amp-hour ratings of deep cycle batteries are based upon a discharge rate at 1/20 of  battery capacity. This is expressed as “C over 20".  A marine battery rated 200ah at C20, discharged continuously at 10 amps, at 80o F., will sustain that load for 20 hrs.  Engine starting batteries are designed for  20% DoD, gel cells  25%, "deep cycle" batteries from 50% to 80% and flooded NiCds 100%.

Starting batteries perform poorly for communications  because they are designed for short periods of high load.

Deep cycle batteries are much better.  A 100w VHF repeater, drawing 20 amps on transmit, requires a minimum 100ah battery to stay within a C20 discharge rate, at 80o. F.

At lower temperatures available capacity is reduced.  Lead-acids lose 50% of their capacity at 32oF!

More rapid rates of discharge, (such as using a marginally sized battery for the load) further reduce available capacity and the number of charge-discharge cycles the battery will provide.  A BCI Group U1 (25 lb., 31ah) gel cell is well balanced to power an FM mobile at 25% duty cycle, medium power transmit, requiring about 6A for 25w, approximating C20 rate of discharge.  If Tx output is increased to 50w, current load increases to 10 amps, a mildly oversized load approximating C10.  This is OK for intermittent surge use, but so stressing a battery frequently such as this will shorten the life cycle of a gel cell!  Deep-cycle, flooded lead-acid tolerate C10 with some loss of life cycle. A portable battery pack designed for C10 discharge rate should be of  "deep cycle" type rated for 50% depth of discharge, such as the AGM-fire resistant, valve regulated types used in portable automatic defribrillators.

A good rule of thumb for sizing a battery systems for a C/20 discharge rate is to ensure one amp-hour per watt of transmitter output.  Estimate the amp-hour capacity required to run your station for 24 hours by summing all loads: transmit current times total operating time times duty cycle, plus receive current with squelch open times standby time and repeat for each piece of equipment.  Then multiply the total loads by 150% safety factor.  If you are too lazy to actually run the numbers, use the amp-hour per watt rule for each 12 hour operational period.

Lead-acid batteries consist of lead alloy grid plates coated with lead oxide paste, immersed in a solution of sulfuric acid.  In manufacture the plates are subjected to a "forming" charge which causes the paste on the positive grid plates to convert to lead dioxide. The paste on the negative plates converts to "sponge" lead.  Both materials are highly porous, allowing electrolyte to freely penetrate the plates.  Plates are alternated in the battery, with porous, nonconductive separators between them, or with each positive plate surrounded by an envelope, open at the top.  A group of negative and positive plates with their separators makes up an element. When immersed in electrolyte, an element comprises a battery "cell."

In lead acid batteries each cell is nominally 2 volts.  Multiple cells are connected in series to increase voltage.  Larger or more plates increase amp-hour capacity, but not voltage. Thicker or fewer plates per cell allow more cycles and longer life for the battery.  The lower the antimony content in the plates, the lower the internal resistance and the less resistant the battery is to charging.  Less antimony also reduces water consumption through electrolysis.  Pure lead plates may break during transportation or service operations requiring removal of the battery.   More antimony allows deeper discharge without damage to the plates and longer service life.

The plates in most automotive batteries are 2-3% antimony and deep cycle batteries 5-6% Sb.  Calcium or strontium used in sealed lead-acid batteries offer the same benefits and drawbacks as antimony, but reduce self discharge when a battery is stored without being used.  Do not exceed 25% DoD with Pb-Ca batteries, i.e. gel cells!

Cells in lead-acid batteries are vented to permit hydrogen and oxygen to escape during charging and to provide an opening for replacing water lost due to electrolysis.  Open caps are common in flooded batteries, but some are flame arrester type to prevent a flame outside the battery from entering the cell.  "Recombinant" caps contain a catalyst which causes hydrogen and oxygen liberated during charging to recombine into water, reducing the need to replace water lost from the battery.   These are recommended for stationary batteries in seasonal equipment which left for long periods on a maintenance level float charge or to be used in photovoltaic systems.

The percentage of acid in battery electrolyte is measured by its specific gravity (Sg).   Only batteries which use acid electrolyte can use specific gravity as a measurement of the state of charge.  A hydrometer is used to measure how much the electrolyte weighs compared to an equal quantity of water.  The greater the state of charge, the higher the specific gravity of the electrolyte. The lower the state of charge, the weaker the acid and the lighter the electrolyte.  Differences in acid density are measured by the float in a hydrometer, which rises higher in an electrolyte sample of high Sg than in one with a lower Sg.

Measuring Sg of a wet, lead-acid battery during discharge is a good indicator of the state of charge.  A fully charged battery has an Sg of 1.265 grams per cubic centimeter, at  75% charge 1.225, 50% charge 1.19 and fully discharged 1.120.  During charging of a flooded battery Sg  lags the charge state because complete mixing of the electrolyte does not occur until gassing commences near the end of the charge cycle.   Because of uncertainty of mixing, this measurement on a fully charged battery is a better indicator of the health of a cell.  Therefore, Sg is not the absolute measure of capacity, but is considered in combination with load testing and open circuit voltage.  Lead-acid batteries accept only about 1/10 of the charging current at 30 degs. F which they will accept at 80 degs. F.

Lead-acid batteries at normal ambient temperature should be charged current from 1/10 to 1/20 of capacity. When not in service, all lead-acid batteries self- discharge at rate of about 5% per month.  The rate of self discharge increases with the temperature. If  a lead-acid battery is left in a deeply discharged condition for a long time it becomes "sulfated" as sulphur in the acid combines with lead from the plates to form lead sulphate.

Auxiliary batteries  require a charge controller to provide regulated, low-level current to compensate for self discharge and protect against sulfation.  They also require regular testing, inspection and replacement of lost electrolyte.

If water is lost during charging and not replaced, the process of sulfation is accelerated in those plates which are partially exposed to air.  "Treeing" is a short circuit occurring between positive and negative plates.  This may be caused by manufacturing defect or rough handling resulting in misalignment of the plates and separators. "Mossing" caused by circulating electrolyte bringing particulates to plate tops can also cause a short.

Sealed, flooded (wet) lead-acid batteries are also called "maintenance free" and experience less self-discharge.  They contain lead-calcium or lead-strontium plates to reduce water loss and usually have catalytic recombiners to reduce water loss and sealed, valve regulated vents.  Sealed-flooded lead-acids tolerate the same temperatures as unsealed batteries, but because Sg isnt readily measured, some sealed-wet batteries are provided with a captive float hydrometer in the electrolyte.  Sealed-wet batteries are common for automotive starting, but should not be discharged below 25%, or their life is greatly curtailed.

Sealed lead-acid (SLA) batteries include gel cells and absorbed glass matt (AGM), have stabilized or "starved" electrolyte, are valve-regulated and completely sealed.  Because there is no free liquid electrolyte to spill, the battery can be used safely in any position.  SLAs are much safer than flooded types for indoor use and in sensitive equipment such as computer uninterruptible power supplies, which would be damaged by exposure to acid fumes.  Any sealed battery will vent if overcharged to the point of excessive gassing, because the valves are designed to purge extreme pressure building up inside the battery case.

Automotive chargers intended for flooded batteries must not be used to charge gel cells unless they have voltage limiting circuitry to preclude their exceeding 14V during charging.  Self discharge of gel cells is minimized by storing them in moderately cool areas of 5 to 15 degs. C.

Gel  cells are NOT deep cycle.  A DoD of greater than 25% significantly reduces their life.  Gel cells must not be used below -20 degs.C, in engine compartments of vehicles or in use subjecting them to temperatures above 50 degs. C.

Absorbed glass matt (AGM) batteries are deep cycle, can be quickly-recharged with no current limit and provide a broad operating temperature range.  Their extreme depth of discharge equals flooded NiCds, but with virtually no maintenance and low life cycle cost.  New aviation AGMs are substantially more expensive than flooded deep cycle batteries of equal capacity, but are much less expensive than flooded NiCds.  Marine or emergency vehicle AGMs such as Lifeline or Optima are not prohibitively expensive, have aviation type cell construction and are recommended as auxiliary power for emergency communications systems.

Flooded nickel cadmium (NiCd) batteries have a physical structure resembling lead-acid batteries, but use nickel hydroxide for the positive plates, cadmium oxide for the negative plates and a potassium hydroxide electrolyte.   Flooded NiCds such as used in military aircraft are not subject to sulfation.  Cell voltage of a typical NiCd is 1.2 volt, rather than 2 volts per cell as for a lead-acid.   Flooded NiCds can survive freezing and thawing without any affect on performance and are less affected by high temperatures.  Self-discharge of flooded NiCds is  3%-5% per month.

Flooded NiCds  can be totally discharged without damage and their ability to accept charging is less affected by the ambient temperature than for lead-acids.  Their lower maintenance cost and longer life cycle makes them a logical choice for repeater back-up systems in remote or dangerous locations.  However, flooded NiCds cant be tested as accurately as a "wet" lead-acid battery, because specific gravity of the electrolyte does not change with different charge states.  If constant charge monitoring is a requirement, flooded NiCds are NOT the best choice.

Dry NiCds used in portable transceivers require care to avoid deep discharge, which causes cell reversal or overcharging, which results in irreversible diminished capacity due to heat damage.  Most amateurs are overly concerned about their dry NiCds developing "memory" from being left charged for a long time.  Most dry NiCds do not fail from "memory," but from prolonged over-charging.   Always bring a discharged dry NiCd pack back at a slow controlled rate, but dont charge more than 14 hours.  A cell which has developed memory or which has been overcharged can usually be restored by one deep discharge/recharge cycle as long as it doesn't out-gas.  A weak NiCd must never be used without recharging, as irreversible damage occurs inside a discharged dry NiCd when a load is applied to it.

The use of properly sized wire and appropriate connections is important in DC power systems.  DC polarity must be maintained throughout the system, as must color coding conventions of wire insulation: positive-red, negative-black and equipment ground-green or bare, following the wire color conventions used in automobiles.

DC Wire gages are much larger than in AC systems, because undersized wiring causes excessive voltage drops which result in loss of available power, which causes some loads to work poorly, or not at all.  For instance, if too small a wire gage is used between a charge controller and battery, the voltage drop measured during full charging rates reduces the set-point the battery is recharged to, reducing operating capacity and life cycle.

To minimize the effects of voltage drop, keep cable runs as short as possible.   For instance, in a 12-volt system with a 10A load, such as typical 2-m mobile transceiver, the AWG #14 wire normally provided results in a 5% voltage drop over 11 ft.  AWG #10 has a 2% drop over the same

distance and 5% drop over 18 ft.  If you must extend the battery leads to reach a trunk-mounted transceiver, use wire  2 gages larger for as much of the distance as possible.

Splice connections must be secure and able to withstand vibration, moisture and corrosion.  Splices up to AWG#8 should be overlapped for a length not less than five times their diameter, spiral wrapped at least three turns, soldered, covered with shrink wrap or electrical tape and then waterproofed.  Larger gage wires should be overlapped and connected with split bolts, soldered, covered with electrical tape and then waterproofed.

Batteries are connected in series to increase voltage or in parallel to increase their amp-hour capacity.  These interconnected groups of batteries are called "battery banks."  To determine the size of the battery bank needed, determine the daily power requirement in watt-hours times the number of days of autonomy that the equipment must operate the loads without re-charging, plus a 30% safety factor (to ensure the batteries are not damaged from excessive discharge).  To convert watt-hours to amp-hours, divide by the voltage.

Always be careful around battery banks!  Even when partially charged, an interconnected battery bank can deliver sufficient voltage and current to arc weld!   Keep sparks and other ignition sources away at all times.  Never allow tools to fall onto terminals or connections.  Never permit construction or use of shelves above the batteries.  Battery banks must always be adequately vented.

When paralleling batteries, reduce the effects of voltage drops which cause unequal resistances between parallel  branches, so that all batteries in the system operate at an equal current and voltage level.  Use the same length of cable from each battery terminal to a central junction point.  Positive and negative do not necessarily have to be of the same length.  This eliminates uneven voltage drop between batteries.  Cable size is calculated based upon the peak charging and load current demands of the system multi-plied by the resistance of the wire.  Marine grade or multi strand welding cable of AWG #8 or larger is recommended.

Most battery problems are caused by oversized loads or equipment operating at excessive duty cycle for too long.

When batteries remain in a low state of charge, check the load as well as the batteries and charging system!  The four ways to determine the charge state of lead-acid

batteries, in declining order of accuracy are:

1     hydrometer / refractometer

2     actual equipment load test

3     artificial load test

4     open circuit voltage

When using a hydrometer you are working with strong acid.  Wear eye and face protection and rubber gloves.  Have baking soda and plenty of fresh water ready to neutralize spills.  To use a hydrometer, squeeze the bulb while the inlet tube is still above the electrolyte level.  Then lower the hydrometer into the electrolyte and slowly release the bulb to draw in the electrolyte.  At the first cell being checked, fill and drain the hydrometer three times before removing a sample.  This brings the hydrometer to the same temperature as the electrolyte.  Take a sample and allow the bulb to fully expand.  The sample must be large enough to completely support the float.

Hold the hydrometer straight up and down, so that the float does not touch the sides, top or bottom of the tube.  Look straight across the electrolyte level to read the float.  Ignore the curve of the electrolyte on the sides of the hydrometer.  Be careful not to drop the hydrometer or allow acid to drip out of it. After reading the hydrometer, to empty it slowly squeeze the bulb again with the inlet inside the cell, but just above the electrolyte level to reduce risk of spills.  Record    the Sg of each cell on a work sheet.  After use, rinse the hydrometer with fresh water at least five times to flush out any acid.  Allow it to dry completely before using it again.

Temperature compensation is required for batteries not at 80 degs. F.   Use an accurate glass thermometer and immerse only the thermometer bulb into the acid, leave it for 5 minutes, read it and then rinse in clear water.  For every 10 degs. F above 80 degs. F a factor of 0.004 must be added.  Subtract the same factor for each 10 degs. below 80 degs. F.  As an example, if  a battery at 30 degs. F has an Sg of 1.240, the battery is 50 degs. below the standard, so the compensation is subtracted from the specific gravity.  The compensation to be subtracted is .004 x 5 = .020; so 1.24 - .020 = 1.220.  A refractometer is the most accurate way to measure electrolyte Sg, requires only a small amount of fluid and is automatically temperature corrected.  Refractometers are compact, rugged and recommended for ongoing maintenance of large auxiliary power systems.

To test the no-load, open circuit voltage an accurate DC voltmeter is required.  Operate the loads from the batteries for five minutes to remove any surface charge the battery plates may have.  Turn off all loads and disconnect the batteries from the rest of the system.  Now measure the voltage across the terminals of every battery.  Open circuit voltage without any load is a good preliminary indicator of

the state of charge.  The open circuit voltage of a fully charged 12-volt battery is over 12.72 volts, whereas it is about 12.6 at 75%, 12.48 at 50%, and 12.12 at 25%.

To perform a load test, after recording no-load voltage, re-connect the system, but leaving float chargers, charge controllers or solar arrays disconnected.  Operate the equipment at normal duty cycle for an hour, disconnect the batteries and measure the battery voltages again.  If any battery indicates a voltage of 10 percent higher or lower than others, it should be serviced or replaced.  An automotive load tester can be used, although you must be aware that this places a large artificial load on the batteries for a short time rather than waiting for a small load to slowly discharge the batteries.  Because available capacity is reduced at faster rates of discharge, this test is not as reliable for communications use as one at operating load.

Accurate trouble shooting requires that all batteries in a bank and individual cells of unsealed, wet-type batteries be numbered.  Recording a system history identifies patterns and trends and is a great time saver for others who may service your system in an emergency, because they  can focus first on the most frequent problems and can anticipate the proper tools and materials to bring.   Battery systems not used on a regular basis must be checked in the spring and fall, at minimum.  Monthly is recommended.

First disconnect all loads.  If battery tops are wet or dirty, remember that fluid on top of the battery is highly acid electrolyte! Clean battery tops with a cloth or brush and a baking soda and water solution.  Rinse with clean water and dry with a clean cloth.  Remove the caps from all cells, check the electrolyte level of every cell in every battery and add distilled water to the fill line on the battery, or " above the top of the plates.  Determine the batterys state of charge with a hydrometer.  Discolored, odorous electrolyte indicates contamination caused by adding other than  distilled water, which results in battery failure.  Inadequate charging without adding water can result in lead sulfate shorts between the plates, cracked partitions between cells and leakage which require the battery to be replaced.

NEVER hammer cable connections onto terminal posts! This breaks fragile spot welds between terminal posts and plates, causing shorts, which could cause a spark and ignite free hydrogen gas, causing an explosion!   Inspect all caps for sound good condition, replace and tighten securely by hand only.   Tighten battery tie-downs securely, but not so tight as to distort the case.

Batteries that will not accept a charge may have had their electrolyte boiled off from prolonged overcharging, or become sulphated by being left at a low state of charge for too long or have suffered  physical damage and should be replaced.  Inspect and repair any corroded, loose or burnt connections and blown fuses.  Cartridge fuses don’t look different when they are blown, so remove them and check continuity with an ohmmeter. A blown fuse shows an infinite reading, a zero reading means it is still intact.

Always determine why a fuse blew before replacing it. Proceed logically, check the most obvious things, such as  r excessive voltage drop at the load. Knowing what failed is necessary to avoid repeating the condition causing the failure.  If  the same fuse blows again, don’t consider the system operational  until everything has been checked out.

Portable Generator Basics And Safety

If you can’t recharge your batteries when the grid is down after a disaster, they are useless.  Generators frequently come to mind, but are not the only answer.

If you don’t know what you are doing, stay away from generators, because a screw up may kill you!

NEVER connect a portable generator to house wiring unless a transfer switch has been hard-wired into the breaker panel to disconnect the house wiring from the AC mains to prevent back-feed when the mains come back up.  Installing one is a job for a licensed electrician.  Ensure adequate earth ground for your personal safety.  Never run a generator in standing water or work on the generator or feed lines while standing on wet ground.

Never run a generator inside an enclosed building because it is impossible to adequately ventilate carbon monoxide and fumes.  Use only UL-listed 3-wire extension cords.  Always plug cords into equipment first before connecting them to the generator feed.  Medical devices and computers require clean power and should never be run direct from unconditioned generator feeds.

Gasoline generators produce about 600w at 120 volts AC for each engine horsepower.  A typical HF transceiver requires about 1200 AC watts at 120 volts.  Generator  capacity must be sized to not only the running wattages of the equipment, but also the starting loads.  For low-loads such as furnace fans multiply running wattages x 2, for  pumps or compressors multiply the running wattages x 7.

A  3.5 HP generator is about the minimum recommended for ACS or RACES use.  It can be carried by one person, uses 5 gallons of gas every 24 hours and produces about 2 kW.  It can power a modest station, such as a barefoot 100w-SSB or dual-band FM mobile, laptop, TNC, a couple small NiCd chargers, an automotive battery charger and limited emergency lighting.  Don’t expect it to also power your 180-watt VHF amp, refrigerator, hot plate and coffee pot!  Light-duty recreational generators are not rated for continuous duty, may quit and not restart when hot, under prolonged disaster conditions.  They should be limited to intermittent use for battery chargers, emergency lighting, cooking and limited use of  power tools.

The minimum generator to power an average house or an emergency command post is 5kW.   A commercial grade, continuous-duty generator of this size has an 8 HP engine, weighs 200 lbs., produces 32A at 120 volts and runs 8 to 10 hours on 5 gallons of gas and requires a 55-gal drum of clean gas every 3-4 days.  A large generator is practical only if you have a reliable source of clean fuel.

It is unsafe to store more than one 20L (5 gal) Jerry can of gasoline in a barn or shed.  Stored gasoline goes bad in a few months unless treated with a stabilizer.  Store Jerry cans empty.  When a hurricane Watch changes to a Warning, fill your cans while there is still power to run the pumps, then store them under cover, and tied down outside! Once the generator is started, use a wooden dip-stick to check fuel level every 2 hours and top off tanks before they run out.

Photovoltaics Make the Most Sense

Photovoltaics produce DC electricity from sunlight and are ideal for maintaining battery banks against self-discharge during extended periods of non-use.  Properly designed solar arrays can provide sufficient current to run communications equipment directly or to maintain battery  banks at operating capacity during periods of heavy load.

A photovoltaic panel producing a current of  from 1% to 1%  of  battery capacity is recommended to compensate for self-discharge in storage batteries and can maintain them on float indefinitely.  No charge controller is required  because maximum current doesnt reach the threshold to evaporate electrolyte after full charge is reached.  A diode is wired in series with the panel to prevent battery discharge at night when panel voltage drops below battery voltage.  This method of float charging is recommended for storing   vehicles or equipment which are not used at least monthly.

Additional panels may be added to the system to replace energy consumed daily by the loads and to compensate for energy used by charge controllers, etc.  To avoid over-charging the batteries during periods of non-use, a charge controller is required to disconnect the panels from the batteries when they reach a fully charged state.

While voltage is nearly constant, the charging current produced is dependent upon incident light in watts per square meter under operating conditions. Under ideal conditions (full sun perpendicular to the panel in clear sky at 20 degs. C) this figure is about 800w/m2..   A 50w panel produce 1,500+watt /hours of energy weekly under full sun or more under  ideal laboratory conditions, but  only a fourth as much during a cloudy mid-Atlantic winter.

To properly size a photovoltaic system adequate to operate continuously, total all loads in watts, multiply by the average daily use in hours, plus a 30% allowance for DC line losses.  Subtract the average daily energy produced by back-up generators and divide the total by the product of the module power rating times the “Area Factor” which compensates for local sun conditions  (4 - in the mid-Atlantic states) to yield the number of panels required.